Suggested Specifications For Series Onyx

CER, CEP, and DEC Electric Pinch Valves

Valves shall be of full cast metal body mechanical pinch type with integral flanges on body and flexible sleeve.  Valve shall be full round (CER and DEC) or pre-pinched (CEP) capable of passing a sphere equal to the diameter (half the diameter for CEP) of the mating pipe.  All internal metal parts are to be isolated from the process fluid by the flexible rubber sleeve.

Valve housing shall be cast iron ASTM #A-126 CL-35, with flanges drilled to ANSI B16.1 Class 125 standard.  Flanges shall have through holes and shall accommodate a standard hex nut per ANSI B18.2.2; tapped flanges are not acceptable.  All bolts used in valve assembly shall be ASTM A 108 grade B5, zinc plated, 80,000 psi min yield / 100,000 psi min tensile strength.  Valve shall be painted per Steel Structures Painting Council Standard #SSPC-SP1-G3 with (2) coats of black interior/exterior Alkyd Enamel to a total thickness of 5 mils minimum.

The rubber sleeve shall be compression molded to insure consistent wall thickness and de-lamination resistance.  Rubber sleeve shall be reinforced with polyester fabric or nylon cords. The rubber sleeve shall be provided with Positive Opening Tabs to insure full opening after the valve has been closed for extended periods of time; tabs shall be fastened directly to the pinch bar with bolts and nuts.

Stem shall be 303 stainless steel with ACME class 2G left hand threads.  To prevent gauling, the stem shall be driven by a bronze alloy ASTM # B 148-65 9B drive nut.  To prevent binding in the event of a sleeve failure, the stem threads shall always remain outside the valve bonnet assembly, and shall be completely isolated from the process fluid, even if the sleeve fails.

Valve shall be operated by a self contained electric actuator.  Actuator assembly shall include an electric motor designed for valve actuation service, thermal overload switches in motor windings, terminal connector, mechanical reversing contactors, anti-condensation heater, local push buttons (Open / Stop / Close), local selector switch (Local / Off / Remote), indicator lights (Open / Close), phase discriminator on 3-phase units, limit switches, torque switches, and an auxiliary hand wheel with automatic de-clutch feature.

Valve shall be designed so that the required one-hand rim pull does not exceed 70 lbf at max rated pressure.  Valves shall be Onyx series CER, CEP, or DEC or approved equal.